## Sheet1
Northern Pulp Nova Scotia mill, in Abercrombie, Pictou County Source Emission Test Results for Summer 2015
The table below provides an overview of the results of the stack testing (source of the emissions) conducted on the Northern Pulp mill. The testing was conducted by Stantec Consulting Ltd., during the period of September 15-18, 2015. Stack tests were taken at two locations: recovery boiler and the power boiler. At the time of testing, emissions of particulate matter from the recovery boiler was 3.9 mg/Rm3, which is well below the stack emission limit of 77 mg/Rm3 as outlined in the company’s 2015 industrial approval. Results for the power boiler were 190 mg/Rm3 which is above the emission limit of 150mg/Rm3.
|  |  | Legend: | does not meet limit
meets limit
unknown
| Stack Emission Limits |  | Source Emission Testing Results
POINT SOURCE | AIR CONTAMINANT |  | AIR CONTAMINANT
| PARTICULATE | TOTAL REDUCED SULPHUR (TRS) | PARTICULATE | TOTAL REDUCED SULPHUR (TRS)
Recovery Boiler | 77 mg/Rm3 | 15 ppm dv (any 4 hour rolling average) | 3.9 mg/Rm3
Lime Kiln | 0.50 kg/adubmt | 20 ppm dv (any 4 hour rolling average) | Not Tested (not required in this round of Source Testing under the Approval) | Not Tested (not required in this round of Source Testing under the Approval)
Smelt Dissolving Tank | 0.50 kg/adubmt | n/a | Not Tested (not required in this round of Source Testing under the Approval) | Not Tested (not required in this round of Source Testing under the Approval)
Power Boiler | 150 mg/Rm3 | n/a | 190 mg/Rm3
High Level Roof Vent | n/a | n/a |  | Not Tested (not required in this round of Source Testing under the Approval)
REFERENCE SAMPLING METHOD | Environment Canada's EPS 1/RM/8 | US EPA Method 16/16A/16B | Environment Canada's EPS 1/RM/8 | US EPA Method 16/16A/16B
mg - | milligrams
Rm3 - | reference cubic meter (ie. The volume of gas at 25 degrees celsius ( °C) and 101.3 kilopascals (kpa) corrected to 11% Oxygen)
ppm dv - | parts per million dry volume
kg - | kilograms
adubmt - | reference production rate in air dried unbleached metric tonnes

## Compatibility Report
Compatibility Report for Copy of NPNS Source Emissions vs Limits 20140922SVrevised.xls
Run on 24/09/2014 9:18
The following features in this workbook are not supported by earlier versions of Excel. These features may be lost or degraded when opening this workbook in an earlier version of Excel or if you save this workbook in an earlier file format.
Minor loss of fidelity | # of occurrences | Version
Some cells or styles in this workbook contain formatting that is not supported by the selected file format. These formats will be converted to the closest format available. | 6 | Excel 97-2003